## FLOCALC
PIPE INCOMPRESABLE FLUID PRESSURE DROP CALCULATIONS
| Input Data | [9 empty] | If a Yield Stress Fluid
| Flow Rate, gpm = | 13 | Q | [9 empty] | Fluid Yield Stress, pascals = | 0 | t | Newtonian Fluid
| Diameter, inches = | 0.785 | D | [9 empty] | Infinite Shear Visc, mPa-sec = | 1 | h |  | 13.0001 | 53.0811
| Length, feet = | 100 | L | Friction
| Absolute Roughness, inches = | 0.001 | e | System Curve
| Density, lbm/ft³ = | 62.43 | r | GPM | Vel | Nre | Frict Fac | AppVisc | Pres Drp | Head, ft
| Viscosity, cp = | 1 | µ
|  |  |  | 0.13 | 0.086172 | 523.6612 | 0.030554 | 1 | 0.0093481 | 0.026358
|  |  |  | 1.3 | 0.86172 | 5236.6123 | 0.0095825 | 1 | 0.29318 | 0.82664 |  | Fittings and Valves
| Output Data |  |  | 2.6 | 1.7234 | 10473.2246 | 0.0081109 | 1 | 0.99262 | 2.7988
| Turbulent Flow |  |  | 3.9 | 2.5852 | 15709.8369 | 0.0074514 | 1 | 2.0518 | 5.7852 |  |  | No. of 45° ELs = | 0 | n
| Mean Velocity, feet/sec = | 8.6172 | V | 5.2 | 3.4469 | 20946.4492 | 0.0070587 | 1 | 3.4554 | 9.7429 |  |  | No. of 90° ELs = | 4 | n
| Reynolds Number = | 52366.123 | Nre | 6.5 | 4.3086 | 26183.0615 | 0.0067927 | 1 | 5.1956 | 14.6496 |  |  | No. of TEEs = | 4 | n
| Friction Factor = | 0.0061532 | f | 7.8 | 5.1703 | 31419.6738 | 0.0065985 | 1 | 7.2677 | 20.4921 |  |  | No. of Check Valves = | 0 | n
| Relative Roughness = | 0.0012739 | e/D | 9.1 | 6.032 | 36656.2861 | 0.0064493 | 1 | 9.6686 | 27.2617 |  |  | No. of Gate Valves = | 0 | n
| Shear Rate, sec-¹ = | 1053.8221 | r | 10.4 | 6.8938 | 41892.8984 | 0.0063308 | 1 | 12.3962 | 34.9524 |  |  | No. of GlobeValves = | 0 | n
| Apparent Viscosity, cp = | 1 | µ | 11.7 | 7.7555 | 47129.5107 | 0.0062339 | 1 | 15.4489 | 43.5599 |  |  | Fixed Drop, lbf/in² = |  | DR
| Pipe Pressure Drop, lbf/in² = | 18.8257 | DR | 13 | 8.6172 | 52366.123 | 0.0061532 | 1 | 18.8257 | 53.081
| Fittings Pressure Drop, lbf/in² = | 4.1871 | DR | 14.3 | 9.4789 | 57602.7353 | 0.0060847 | 1 | 22.5256 | 63.5132
| --------------------------------------------------- |  |  | 15.6 | 10.3406 | 62839.3476 | 0.0060258 | 1 | 26.5479 | 74.8547 |  |  | Vel Hds | 101.2 | N
| Total Pressure Drop, lbf/in² = | 23.0128 | DR | 16.9 | 11.2023 | 68075.9599 | 0.0059746 | 1 | 30.8922 | 87.1038 |  | X | Equiv L | 22.2417 | Le
| Total Friction Loss, ft-lbf/lbm = | 53.081 | h | 18.2 | 12.0641 | 73312.5722 | 0.0059296 | 1 | 35.558 | 100.2595
|  |  |  | 19.5 | 12.9258 | 78549.1845 | 0.0058898 | 1 | 40.5449 | 114.3207
| Input in Red | [10 empty] | Input Examples
Output in Blue
Sprinkler Water Line: 13 GPM, 0.785" Diameter Tubing, 100 ft long - Newtonian Fluid
TiO2 - Water Slurry: 500 GPM, 3.0" Diameter Pipe, 100 ft long - Yield Stress Fluid
Fluid Yield Stress = 20 pascals,
Infinite Shear Viscosity = 176 mPa-sec

## DEFINITIONS
YIELD STRESS FLUID RHEOLOGICAL DEFINITIONS
µISV
1
µA
1
Shear Rate R = 8V/D, sec-1
µISV | = Infinite Shear Viscosity, mPa-sec
µA | = Apparent Viscosity, mPa-sec
= Slurry Yield Stress, Pascals
= Shear Stress of fluid flowing with a shear rate, R = 8V/D, sec-1
V | = Average fluid velocity, ft/sec
D | = Pipe inside diameter, ft
Flow Condition
Shear
Stress
in
Pascals
o
o